## Sheet3
# | lat | long | Case Study | Country | Location | Contributor | Date | Background | The UV System | Outcomes and Lessons Learned | Pictures
1 | 37.5726 | -85.1551 | The Water On Wheels Mobile Emergency Water Treatment System | USA | Western Kentucky following multiple tornadoes in December 2021 · Graves County Public Health Department · Mercy Chef Mobile Kitchen · Dawson Springs 4H Camp Ukraine in Summer 2022 (still operating at multiple sites) Eastern Kentucky following flooding in multiple communities in August 2022 (with sites still operating) · Perry County, HomePlace Community Center · Perry County, Buckhorn Children’s Home · Letcher County, Mayking Fire Department · Breathitt County, River Caney Staging Area | James A. Goodrich, Ph.D. [1], Kurtis T. Daniels [2], Mark Hogg [3], Gregory Sayles, Ph.D. [4] [1] Sr. Science Advisor, USEPA, Office of Research and Development, Center for Environmental Solutions and Emergency Response, Corresponding Author [2] Vice President, Director of Field Operations, WaterStep [3] Founder and CEO, WaterStep [4] Director, USEPA, Office of Research and Development, Center for Environmental Solutions and Emergency Response | Western Kentucky following multiple tornadoes in December 2021 · Graves County Public Health Department · Mercy Chef Mobile Kitchen · Dawson Springs 4H Camp Ukraine in Summer 2022 (still operating at multiple sites) Eastern Kentucky following flooding in multiple communities in August 2022 (with sites still operating) · Perry County, HomePlace Community Center · Perry County, Buckhorn Children’s Home · Letcher County, Mayking Fire Department · Breathitt County, River Caney Staging Area | Following a natural or manmade disaster, a community’s water treatment plant or distribution system may be rendered incapable of providing safe water to all or portions of their drinking water distribution system. The Water On Wheels Mobile Emergency Water Treatment System (WOW Cart) is designed to provide treated water during the a response and recovery period after a disaster. It is designed for deployment anywhere in the world and can provide potable water using sources ranging from raw water to compromised water from distribution systems. Recent deployments include: · Western Kentucky following multiple tornadoes in December 2021 o Graves County Public Health Department o Mercy Chef Mobile Kitchen o Dawson Springs 4H Camp · Ukraine in Summer 2022 · Eastern Kentucky following flooding in multiple communities in August 2022 (with sites still operating) o Perry County, HomePlace Community Center o Perry County, Buckhorn Children’s Home o Letcher County, Mayking Fire Department o Breathitt County, River Caney Staging Area | The WOW Cart essentially replicates a conventional water treatment system with the added benefit of UV disinfection. Unit processes include filtration, GAC adsorption, UV-C LED and gas chlorination. The UV disinfection (LEDs at a wavelength of 280 nm, operated from a 24 V DC input) provides a dose of around 40 mJ/cm2, which complements the chlorination step in its ability to inactivate microbial contaminants that chlorine is unable to address. The WOW Cart produces approximately 10 GPM and can be operated off-grid using the supplied dual fuel gasoline/propane generator or by plugging it into a normal wall outlet. The footprint and weight were minimized during design to enable transportation in the back of a pickup truck and movement on-site by two people. It is expected that following deployment, the WOW Cart will be warehoused following complete drainage and drying out until needed for the next response. | Various deployments have successfully provided safe water for thousands of people to drink, bathe, wash clothes and prepare food. From this work, the main impediment for more widespread adoption of mobile emergency water treatment, including UV, is not technological. It is acquiring government pre-approvals and integration into existing State or Federal emergency procedures. Awareness, knowledge, and acceptance of inexpensive, easy to operate and deployable mobile water treatment systems at the government level is also needed. | 1a.jpg 1b.jpeg 1c.jpg 1d.jpg 1e.png 1f.jpeg 1g.png 1h.jpg 1i.jpg 1j.jpeg
2 | 22.3 | 78.66 | UVWaterworks, India | India | Several sites in India including in Bhupalpur | Ashok Gadgil, University of California, Berkley | First device was tested at several sites in India including in Bhupalpur throughout 1994-1995 | This project was conceived in the summer of 1993 during an outbreak of a mutant strain of cholera in India (“Bengal” Cholera) against which there was no vaccine. Using funds from Dr. Gadgil's Pew award and $10,000 each in seed funding from USAID and from LBNL's Center for Building Science, we reviewed existing technologies, initiated a design effort, and held a workshop in Washington, D.C. in November 1993, to address the issue. Our goal was to design a low-cost, low-maintenance, and robust system for disinfecting communities’ drinking water collected from surface water sources or handpumps. | UV Waterworks has created a uniquely affordable and effective device: disinfecting water using the equivalent of a 40-Watt light bulb at a cost of 2 cents per ton of water treated, treating 15 liters (or approximately 4 gallons) per minute, enough for 500-1500 people. Specific capabilities of the device include: 1. Works with unpressurized water 2. Deactivates bacteria and viruses in clear water using a low-pressure UV lamp 3. Does not need a trained operator 4. Maintenance every 6 months 5. Rapid disinfection (water passes through unit in 12 seconds) Limitations of the device include: 1. Does not treat non-biological water pollution (chemical/mineral content) 2. Does not treat Giardia or Cryptosporidium (these must be filtered out) 3. Does not treat turbid water (again, water must be pre-filtered - the same filter that removes Giardia and Cryptosporidium should be sufficient to remove turbidity) 4. Does not provide residual protection - water can be re-infected through improper handling 5. Does not work without electricity - where grid power is not available, photovoltaic panels or other renewable energy source would raise the cost from 10 cents to 40 cents per person per year. These costs include the full annualized costs, including electricity, consumables, and amortization. | The organizational component of the public sector approach in this case provides several important lessons. Despite a well-organized half-day executive dialogue roundtable, sponsored by USAID and attended by 21 representatives from UNICEF, WHO, several NGOs and other interested organizations, next steps in development remained undefined, largely due to the lack of an established route to deployment. Without a consensus on how to deploy affordable water treatment technology in under-funded communities, money can't be spent, and systems can't be installed. This organizational and financial challenge with respect to public sector involvement is as apparent in 2022 as it was 1996. | 2a.jpg 2b.jpg 2c.jpg 2d.jpg 2e.jpg
3 | -29.8618 | 31.0099 | UVWaterworks, South Africa | South Africa | A rural area near Durban, South Africa, at a hospice for abandoned infants who have tested positive for the HIV antibody | Ashok Gadgil, University of California, Berkley | Installed July 1997 | In 1993, UV Waterworks set out to design a community water system in response to a cholera outbreak in India at the time. Following the acclaim of that project, a second field test of the UV-based water treatment system was conducted in Durban, South Africa. After an initial test using municipal laboratory facilities in Durban, the device was installed at a hospice for abandoned infants who have tested positive for the HIV antibody. Safe drinking water is critical for these children in improving the chances of living with HIV. | UV Waterworks has created a uniquely affordable and effective device: disinfecting water using the equivalent of a 40-Watt light bulb at a cost of 2 cents per ton of water treated, treating 15 liters (or approximately 4 gallons) per minute, enough for 500-1500 people. Specific capabilities of the device include: 6. Works with unpressurized water 7. Deactivates bacteria and viruses in clear water using a low-pressure UV lamp 8. Does not need a trained operator 9. Maintenance every 6 months 10. Rapid disinfection (water passes through unit in 12 seconds) Limitations of the device include: 6. Does not treat non-biological water pollution (chemical/mineral content) 7. Does not treat Giardia or Cryptosporidium (these must be filtered out) 8. Does not treat turbid water (again, water must be pre-filtered - the same filter that removes Giardia and Cryptosporidium should be sufficient to remove turbidity) 9. Does not provide residual protection - water can be re-infected through improper handling 10. Does not work without electricity - where grid power is not available, photovoltaic panels or other renewable energy source would raise the cost from 10 cents to 40 cents per person per year. These costs include the full annualized costs, including electricity, consumables, and amortization. | The organizational component of the public sector approach in this case provides several important lessons. Despite a well-organized half-day executive dialogue roundtable, sponsored by USAID and attended by 21 representatives from UNICEF, WHO, several NGOs and other interested organizations, next steps in development remained undefined, largely due to the lack of an established route to deployment. Without a consensus on how to deploy affordable water treatment technology in under-funded communities, money can't be spent, and systems can't be installed. This organizational and financial challenge with respect to public sector involvement is as apparent in 2022 as it was 1996. | 3a.jpg 3b.jpg 3c.jpg 3d.jpg 3e.jpg 3f.jpg
4 | 19.0521 | -70.6316 | Safe Water Access in Rural Cities of the Dominican Republic | Dominican Republic | 4 primary schools within the La Vega region of the Dominican Republic (with plans in 2022 to implement a 5th system in Desecho): El Mamey, La Torre, Las Canas, Los Peladeros. | Rachel E. Gehr [1], Ernest R. Blatchley III [1,2] [1] Purdue University, Division of Environmental and Ecological Engineering [2] Purdue University, Lyles School of Civil Engineering | Program launched in 2012 | A course was developed at Purdue University to support safe water access in rural areas of the Dominican Republic. The project team comprises undergraduate and graduate students primarily studying Engineering, Nursing, and Agriculture. Students work within four committees – Design, Communications, Sustainability, and Monitoring, Evaluation, and Publication (MEP) – to provide community-scale potable water treatment systems, administer water, sanitation, and hygiene (WASH) education, prepare a long-term plan for the systems, and survey the local community on attitudes toward public health practices, respectively. Since its launch in 2012, the Water Supply course has implemented drinking water treatment systems in four primary schools within the La Vega region of the Dominican Republic. The current source of drinking, cooking, and cleaning water in these communities is untreated rainwater. | A sand filter is used to remove debris and large particles followed by a 1-micron cartridge filter for removal of microscopic particles, including bacteria and other microbial pathogens. A UV disinfection system inactivates microbial pathogens, including bacteria, viruses, and protozoa, and serves as the primary disinfectant. Zimba, an autonomous, gravity-based chlorinator, dilutes bleach to the desired concentration and provides secondary disinfection for continuous treatment during transportation and storage. The systems deliver an average of 24 L per minute and are powered by solar panels. The operator at each school was trained in-person and given a manual and videos addressing maintenance and troubleshooting. The system produces finished water that is safe for drinking, cleaning, and cooking at the schools, and which can also be routed to a handwashing station. | Treating the rainwater to a potable quality was the easiest of the encountered challenges. The greatest barrier to project success perhaps lies within the choice of installing these systems in elementary schools. Although they are central to the communities both socially and geographically, the academic calendar leaves the systems unused during summer and winter breaks. This lack of operation often results in equipment failure, requiring maintenance or replacement. Operators that know how to resolve these issues often change due to school staff turnover, but new operators are not sufficiently trained after accepting the role. Parents of the schoolchildren have required certifications from Dominican labs proving the water’s potability, but these labs are difficult to find in-country. Finally, no sustainable business model has been developed due to the complication that water cannot be sold from school property. For this type of water system to be implemented in other regions of the DR, the project must gain community investment in the importance of potable water and commitment to operating the system on a daily basis. | 4a.jpg 4b.jpg 4c.jpg
5 | -1.7979 | 29.6524 | The “Bring Your Own Water Treatment System” | Rwanda | Mugonero and Muramba, which are dense sprawls of subsistence farms located near Rwanda’s western border with the Democratic Republic of the Congo | Evan Alexander Thomas, University of Colorado, Boulder | Developed and installed from 2005-2007 | The Bring Your Own Water treatment system (BYOW) was developed between 2005 and 2007 as a collaboration between the University of Colorado at Boulder chapters of Engineers Without Borders (EWB-CU) and the Johnson Space Center (EWB-JSC), to address the unique water treatment needs of two communities in Rwanda: Muramba and Mugonero. These communities are dense sprawls of subsistence farms located in the remote and mountainous region near Rwanda’s western border, and both suffer from inconsistent water supplies from a range of sources, including piped water, harvested rainwater, and surface water. Drinking water from several community sites showed total coliform or E. Coli contamination. Moreover, water is distributed through deteriorating and leaking pipe networks with water quantity and waterborne illness varying dry and rainy seasons. | The Steps of the “Bring Your Own Water Treatment System” are: (a) a gravity feeding inlet bucket (b) either an array of inclined settling tubes or an up-flow gravel roughing filter (c) a rapid sand filter (d) a UV sanitation subsystem with an electronic timer and valve, powered by photovoltaics The system is capable of treating water at 10 LPM. Challenge tested treating activated sludge from a sewage plant in Houston, Texas (USA), the system was shown as capable of reducing turbidity from 70 NTU to below 1, and 3000 CFU/mL to below <2. In the field, a maximum of 4.65 NTU was reduced to below 2.25, and a maximum of 63 CFU/mL to 0 (with the exception of one case, where CFU/mL was reduced to 1). To support its sustained use, significant consideration was given to community consultation, local availability of materials, and local capacity to maintain the system. The systems were installed for free-of-charge use, although future BYOW systems could operate a pay-per-use business model. | Firstly, designing a technology that is maintainable economically and sustainably is paramount, prioritizing the elimination of biological contamination via UV disinfection and then working backwards to designing a full system. Secondly, community adoption is contingent on a number of factors outside of water treatment, the provision of other technologies contributing to a perception of a water treatment technology forming part of a suite of community-enriching technologies that is greater than the sum of its parts. Lastly, community adoption is vital not just for use, but for maintenance and reporting, which have been vital for the continued use of the BYOW systems in both the Muramba and Mugonero communities. | 5a.png 5b.png
6 | 11.8811 | -83.8088 | A Community UV Water System in Rama Cay, Nicaragua | Nicaragua | Rama Cay, an island located near Bluefields, Nicaragua | Daniel Ma, Ohio State University & Messiah University (in collaboration with Friends in Action) Project is a collaboration between Friends in Action International and Messiah University | 2018-2022 | Rama Cay is an island located near Bluefields, Nicaragua, with a population of approximately 1,400. Friends in Action International (FIA) is a faith-based, non-governmental organization that has worked in the Rama community for over 15 years. Individual families from Rama Cay previously obtained drinking water by traveling 30 minutes by boat to purchase bottled water at the mainland. In 2018, FIA invited Messiah University student teams to design a water system for the community. Politically, the island functions as two communities, one northern and southern community. Therefore, two water systems were required. Two wells were chosen as sources, located on the northern and southern sides of the island, respectively; and their quality and quantity were tested. Environmental concerns included determining appropriate location for RO brine disposal to avoid disrupting marine life (e.g., shrimp farms and fishing). Operationally, generator-driven electricity is available for 8 hours a day in limited locations. | Each system was designed to provide 400 gallons of drinking water per day, requiring 5 hours of generator operation per day. A submersible well pump delivers water to a multibarrier treatment system that includes prefiltration, reverse osmosis (RO) to remove salts and bacteria, UV disinfection as an additional barrier for microbial treatment, and calcite filters to balance water chemistry. A VIQUA VT4 Model was selected for UV disinfection. At the operating flow rate of 1.38 gallons per minute, the UV system is expected to deliver > 40 mJ/cm2 (for UVT > 75%). The capital cost of each individual water systems was approximately $9,400 USD, and the ongoing parts replacement costs are approximately $700 USD every 2 years. | As of June 2022, the project has been completely designed but implementation has been delayed indefinitely due to political tensions on the island. The students learned the importance of patience in cross-cultural project work as well as the need to adjust academic coursework (e.g. capstone project work) with the rhythms of NGOs and communities in other cultures. For success in development projects such as this, it is imperative to continually rely on NGO relationships with local communities, to demonstrate compassion through heart-felt listening, and to adopt a constant posture of learning. | 6a.png 6b.png 6c.png 6d.png
7 | 10.9094 | 78.3665 | Improvement of Drinking Water Quality from Surface Water Ponds Using a Zero-Energy UVC-LED Reactor | India | Tamil Nadu, South India | Prof. Dr. S. Kanmani, Director, CES, Anna University, Chennai, India | 2018 | In the regions where ground water is either not available, saline, or polluted due to human activity, and rainfall is either limited or unpredictable, people depend on more traditional water harvesting structures, such as Ooranies. Oorani is a Tamil name for a dug-out pond that traps rainwater run-off and stores it for further use. With the growth of technologies like hand pumps and bore wells, Ooranies in the villages of Tamil Nadu, India were often left out without proper care. Due to limited rainfall and the fast depletion of groundwater, the drinking water supply through the modern systems in rural areas faced challenges. This led the Secretary to Government, Rural Development Department to move to renovate the Ooranies to augment the existing water supply. The Center for Environmental Studies, Anna University along with Ministry of Rural Development came forward with an aim to provide clean and safe drinking water for the rural people. In order to achieve the drinking water quality for zero coliforms, disinfection studies had to be conducted using UV LEDs disinfection. The Pattikadu Oorani (Tamil Nadu, South India) was selected for this research, as the Oorani is the only source of drinking water for residents. | An annular UVC-LED photo-reactor (with a 1 L capacity) was designed inactivate pathogens in water from the Oorani. The lever of a Mark II hand pump was connected to a gear wheel and dynamo such that the mechanical energy from its up-and-down motion when being operated was converted into electrical energy. The dynamo then charged a 6V DC battery to power the UV reactor. | The disinfection using UV LEDs offers numerous advantages, including the robustness of the solid-state technology, generally low cost and long lifetime, no chemical usage, low heat generation, and small size compatible with modern trends in miniaturized instrumentation. The electrical power required for the disinfection was taken from the mechanical energy from movement of the hand pump lever, which made this a zero-energy technology for practical applicability for the improvement of drinking water quality. Although this technology is developed for the rural sector, it could be extended to semi-urban, urban, and industrial communities either at household level or at field-scale level for water purification. | 7a.png 7b.png 7c.jpg 7d.jpg
8 | -1.9647 | 30.6444 | A Solar-Powered Water Treatment System for Rural Areas of Rwanda | Rwanda | Several locations in Rwanda | Tonnie Telgenhof Oude Koehorst, Nedap N.V. Groenlo - Netherlands | 2010-present | Nedap set out to design a “pure and simple” solution for drinking water systems in rural areas. During the start of the project, the following challenges were set for this system: usage of present water sources, multi-barrier process, limited storage of water and most important: low costs. Requirements for easy transportation, technical education at user’s level and maintenance of the system were also highlighted. | The Naïade is a stand-alone, solar-powered water purification unit which can be set up and ready for use within 30 minutes. No special infrastructure is required, and a single unit can meet the water requirements of between 250 and 400 people at an estimated cost as low as USD 1,50 per person per year. After prefiltering with 2 washable bag filters of 25 and 10 microns, disinfection is achieved with use of a 20 watt UV lamp (dose of 40 mJ/cm2). A solar panel of 80 W is used so that it can perform independently, even in remote areas without access to electrical energy. The unit has the total weight of 44 kg with the dimensions of 54 x 75 x 140 cm (excluding solar panel). The flow rate is approximately 5 L/min; storage capacity is 100 L. A regular 12V car battery can be used for back-up power during the night and is charged by the systems solar panel. | 23 Naïade units have been installed at schools and small hospitals in Rwanda and maintained by the Impala Foundation and some of these units are operational for over 12 years now. Units were financed by the Dutch Soroptimists organization. The biggest challenge is financing the purchase of units and the maintenance. This has been the case in all countries where Naiade systems were installed (Africa, Asia, South Americas). | 8a.png 8b.jpg
9 | 3.0199 | 32.3883 | A UV-LED Demonstration Unit in Uganda for Drinking Water Disinfection | Uganda | Gulu, located in Northern Uganda in the Western Uganda's Kyegegwa district | Mitch Hansen, Galina Shevyrina, and Oliver Lawal, AquiSense Technologies | 2021-present | Located in inland Africa, between Kenya and the Democratic Republic of the Congo, Uganda has a population of over forty-seven million people. While in recent years there have been strides made by the government and other organizations in an effort towards development, potable water remains a scarce resource. Nearly 70% of citizens are without access to clean water. In Uganda, only half of the healthcare facilities treat water to make it suitable for drinking. Municipal water systems are rare and difficult to install, and bottled water is considered a luxury in the majority of communities. This is where NGOs, such as the African STEM Education Initiative (ASEI), lend a helping hand to local communities. The goal of the ASEI is to provide Ugandan students with the resources needed to advance their knowledge in STEM; therefore, directly aiding in the development of communities that house facilities such as schools and hospitals across the country. One of the primary goals of ASEI is to provide clean drinking water to people, to which will help to promote the lifelong health of children and communities in Uganda. Two PearlAqua AutoMate units, developed and manufactured by AquiSense Technologies, were installed in a healthcare center in Western Uganda's Kyegegwa district and in a primary school in the community of Gulu, located in Northern Uganda, to boost access to clean drinking water. | ASEI used a 12V/20W DC solar system, and in some cases grid electricity. Pre-filtration is done using bio-filters and cartridge filters before it is passed through the UV-C units at a flow rate of 3.5 LPM by Aquisense technologies the selected unite was PearlAqua AutoMate. Regular surveys are done to ascertain performance and do evaluation. ASEI will now integrate UV-C units into modular micro-factories with the ability to produce >50,000 liters of treated water per month, which will be leased to water vendors to sell water at a few cents. | A few things that ASEI has learned through this process and will be implementing in the future is UV-C units and filters need to be enclosed or they are at risk of being destroyed by end users. Specially designed power cables with proper voltage controls should be used or there is a risk that the circuit boards are destroyed. Prior to any installations, it should be ensured that power and water are well managed to limit the possibility of electrical shocks. Looking forward, ASEI is planning on continuing their mission and hopes to broaden the effects of clean drinking water to more people throughout Uganda. | CS1 #1.jpg CS1 #2.jpg CS1 #3.jpg CS1 #4.jpg CS1 #5.jpg CS1 #6.jpg CS1 #7.jpg CS1 #8.png CS1 #9.jpg CS1 #10.png CS1 #11.jpg CS1 #12.png CS1 #13.png
10 | 10.4088 | 122.5629 | A Solar-Powered UV-LED System for Drinking Water Disinfection in the Philippines | Philippines | Panobolon Island, Guimaras, Western Visayas, Philippines | Kumiko Oguma and Bernice Mae Yu Jeco-Espaldon, University of Tokyo | 2018-present | Pilot tests of a solar-powered UV-LED water disinfection system was conducted in Panobolon Island, an off-the-grid island in the Guimaras, Western Visayas, Philippines. Groundwater was harvested from dug wells and then tested for coliform count before and after UV-LED irradiation. The long-term aim is for the island users to learn how to operate and maintain the system themselves for sustainability. On Panobolon Island, we frequently detected E. coli in sampled wells of more than 1 CFU per 100 mL. During our pilot sampling in September 2018, all the 9 selected wells were positive with E. coli. Also, our DNA sequencing of bacterial isolates from a sampled island well suggested the presence of Shigella flexneri, a pathogen which can cause foodborne and waterborne diseases [1]. Because the island has no access to the national power grid, solar-powered UV-LED disinfection system is a suitable technology for islands. [1] Bernice Mae Yu Jeco, Aris Larroder and Kumiko Oguma, “Techno-social feasibility analysis of solar-powered UV-LED water treatment system in a remote island of Guimaras, Philippines,” Journal of Photonics for Energy 9(4), 043105, 2019. doi: 10.1117/1.JPE.9.043105. | The flow-through module used contains a single 280-nm LED, rated to operate at 12V, 350mA. It has a hydraulic retention time of 1.23 s and was designed to disinfect flowing water at 2 L/min. The UV-LED was powered by a 12V-regulated, 150-W commercial Si solar panel. | The following are proposed for the final implementation of the PV-powered UV-LED water disinfection system: 1. A single UV-LED flow-through module was not enough to achieve wild-type E. coli inactivation, as treated water was still E. coli positive on occasion. Another module with higher inactivation performance would be preferable. Or, increasing the number of current module and connect them in cascaded flow configuration would work; 2. Photoreactivation under strong sunlight can be an issue in the field. Sunlight protection measures are to be taken. 3. Seasonal change of both groundwater quality and solar radiation is to be monitored by conducting the field test in the island in a span of at least one (1) year. | 10a.jpg 10b.png 10c.jpg 10d.png
11 | 16.344 | 77.5007 | Development of a UV-LED Water Treatment System for Rural Areas in South India | India | India Karnataka state | Dana Pousty, Hadas Mamane, Igor Donskoy, Ram Fishman, Bhavani Rao | 2022-08-01 | This project was a pre-implementation field-testing of a new UV-LED solution built for rural areas. The objective was to analyze the current state and the effect of the prototype including testing water contamination before/after disinfection, measuring water turbidity, mapping the water sources and consumption behavior, as well as surveying the social aspects and perspective of the implementation | The flow-through module used contains a single 280-nm LED, the system has a hydraulic retention time of 2 s and was designed to disinfect flowing water up to 2 L/min, in this case, the flow rate was 1.5 L/min. The UV-LED was powered by the grid line electricity system which requires an input voltage of 11-14V. | • Consider the entire water journey from source to use - the water sources are not always the problem, as even treated water can get recontaminated during storage. • Water should be treated as close as possible to the point of use - the water disinfection process should not be placed at a distance (too much effort for daily use), it should be either in a close community tap or at the household level. • Depending only on the existing energy sources - solar panels are difficult to install, maintain and operate in these areas, thus energy harvesting could be from diversified options which are case specific as a hydrogenator or a battery. • Count on intermittent electricity a day - the system cannot be dependent on constant electricity supply but can be based on short-term charged electricity. | 11a.png 11b.png 11c.png 11d.png 11e.png 11f.png
12 | 18.2097 | 104.5399 | LP UV Treatment of Wastewater at a Hydropower Facility in Laos PDR | Laos | Theun-Hinboun Hydropower Company Na-Hin Laos | Sara Beck, University of British Columbia | 2011-present | In 2011, a UV disinfection system was installed for decentralized wastewater treatment at the site of an existing wastewater treatment plant at a hydropower dam. The original wastewater treatment plant, in use from 1995-2009 and used a mechanical activated sludge system, had stopped functioning due to high costs and lack of operation and maintenance knowledge and capabilities. As a result, the system had high odors and was no longer meeting effluent wastewater quality discharge standards. | The UV system consisted of four Sanitron ultraviolet water purifiers (Model S50C, 20 GPM) manufactured by Atlantic Ultraviolet Corporation, which used STER-L-RAY low-pressure germicidal lamps, emitting at 254 nm, encased in a stainless-steel chamber. The lamps are horizontal, operated in parallel, in two groups of two (Fig. 2). This particular system also included a Guardian digital UV light monitor, which was installed in the visualization port to detect decreases in UV irradiance from, for example, i) fouling of the quartz sleeves, ii) poor water quality, which would block the UV transmission through the water, or iii) depreciation of the lamp output. | • A suggestion for improving pre-treatment of the water prior to UV disinfection was to install a tube settler in the aerobic pond so that particles would attach to it and settle down. Sand filters and membrane filters would also reduce the influent turbidity; however, they would require routine maintenance. Other suggestions from colleagues at the Asian Institute of Technology were to better maintain the wetlands in the planted gravel filter by harvesting, for example. Ukraine in Summer 2022 (still operating at multiple sites) • A suggestion to increase UV exposure was to route the four lamps in series instead of in parallel; however, the flow rate with the lamps operating in parallel was already exceeding that recommended by the manufacturer. Therefore, routing them in series would not have been sufficient for meeting the demand of the system. Adding more lamps would have been one solution to increase the disinfection capacity while maintaining or lowering the flow rate. | 12a.jpg 12b.jpg 12c.jpg 12d.jpg 12e.png
13 | 25.8041 | -109.0265 | Household UV Disinfection of Drinking Water in Rural Mexico | Mexico | Baja California Sur, Mexico, State of Chiapas, Mexico | Ane Galdos and Fermin Reygadas, Cantaro Azul | 2006-2014, 2018-2022 | From 2006-2014, Cantaro Azul partnered with the University of California (Berkeley) to install UV drinking water disinfection systems for 400 rural households. A second iteration of UV installations was undertaken in 2018-2022 through Cantaro Azul’s SAFEWATER program. Here, 187 treatment units were installed in rural households. | The UV system, called Mesita Azul, was a 5 L/min low pressure UV reactor delivering an estimated dose of 1,200 mJ/cm2 through a 15 W mercury lamp. The lamp was positioned above the water to avoid scaling. Mark III and Mark OS. The treatment process consists of two pleated filters with nominal pore sizes of 5 μm and 1 μm, an activated carbon filter, and a UV disinfection chamber (either the same open-channel system as the Mesita Azul, or a common pressurized system with the lamp submerged in the water and protected with a quartz sleeve). The key element of the SAFEWATER system is that it uses gravity to distribute water from the top container, through ½” PVC pipes to 2 to 5 taps installed within the home. | • It was observed that since the UV system was designed only to treat the drinking water and not water intended for non-potable uses (hand-washing, laundry, etc.), an estimated 50% of the people in the study continued to sporadically drink non-treated water. • This study demonstrated that UV disinfection can offer important advantages over chemical treatment, including not impacting the taste or temperature of water and being able to rapidly treat large quantities of water that can meet all household water needs and reduce the risk of people drinking untreated water. • Scaling UV disinfection in rural communities requires efforts to reduce production costs, increase the lifetime of the products, and integrate such treatment methods into government programs that partially or fully subsidize water treatment solutions in marginalized communities. To achieve this goal, it is important to form alliances that support all dimensions of the implementation of UV, from research and innovation to product design, capacity building, supply chain development, community mobilization, and public policy advocacy. | 13a.jpg 13b.jpg 13c.jpg 13d.jpg 13e.jpg 13f.jpg 13g.jpg 13h.jpg 13i.jpg 13j.jpg 13k.jpg 13l.jpg 13m.jpg 13n.jpg 13o.png
14 | -2.8992 | 31.9903 | UV Treatment in Rural Health Care Facilities in Northern Tanzania | Tanzania | Geita region in northern Tanzania: Kharumwa, Nkome, Kashishi, Nyangh’wale, Nyugwa, Bukwimba | Karlye Wong, University of Toronto | 2019-present | While 54% of rural health care facilities (HCFs) have access to basic water services on premises [1], the safety of the water being supplied and used in healthcare facilities remains a matter of critical concern. Originally, this project was part of a much larger public health project to address high levels of maternal and newborn mortality at hospitals. This intervention consists of seven solar-powered ultraviolet (UV) rainwater harvesting (RWH) systems in HCFs in the Geita region in northern Tanzania, serving a catchment region of over 130,000 people. This was funded by an international agency and implemented by an NGO in 2019. [1] World Health Organization. "WASH in health care facilities: global baseline report 2019." (2019). | At each hospital, rainwater was collected from a large rooftop catchment area. Through a series of gutters, the rainwater passed through a first flush diverter and wash out chamber which addressed dirt, debris, and leaves. The water then stored into a 100 m3 underground storage tank. A solar-powered pump brought the rainwater into a 10 m3 raised storage tank. Water flowed from an elevation, through a 25 W low-pressure UV lamp. The UV lamp was powered by a 125 W, 12 V solar panel, which charged a 12 V lead-acid battery. | • Following the installation of the UV RWH system, the hospitals observed a significant drop in water-borne illnesses and increased satisfaction from service providers from the facility. • They reported increased confidence in their work and satisfaction with their roles due to improved cleanliness of their facilities and the reduction in common infections. • After 18 months, an inspection of the six health care facilities observed that 3 of 7 lamps were not functional at the time of visit • The UV lamps themselves did not provide clear user feedback of their status. This resulted in lamps which overheated from being always on, or not functioning due to burn out or simply being switched off. • In order to ensure sustainability of these projects in low-income settings, it is necessary to consider socio-economic perspectives, governance structures, and community engagement. Implementation must be accompanied with contextualized approaches, technical expertise | 14a.png
15 | -1.9647 | 30.0644 | Carbon Financed Rural Water Treatment | Rwanda | Rwanda | Evan Alexander Thomas, University of Colorado, Boulder | 2007-2010 | The Manna Energy Limited and Portland State University in-line water treatment system was developed as an evolution of the BYOW treatment system in Rwanda between 2007 and 2010. This in-line treatment system was designed to provide a much higher volume of water for communities and schools, up to 100 liters per minute. The system design was motivated by a partnership with the Rwanda Ministry of Education, and designed to be fully funded and maintained through the generation and sale of United Nations carbon credits, offsetting both the actual use and demand for firewood for water boiling. | The design solution is installed in-line with existing water pipes and included an elevated backwash tank, a gravel filter, and a pressurized sand filter followed by a solar photovoltaic powered UV disinfection system. The UV system included two Sterilight UV lamps, a Real-Tech UVT sensor, a flowmeter, and a valve. The electronic controller, designed by Manna Energy Limited and Portland State University engineers, monitored UVT and flowrate and turned the smaller UV lamp on for low flowrates and clear water, then the larger UV lamp on for higher flows and lower water quality, and controlled the flowrate with the valve to maintain minimum UV residence time. | While UV disinfection systems are highly effective at water treatment, they do require electricity, pre-filtration, and monitoring. As such, in many contexts other water treatment systems may be more viable, cost-effective, and fail-safe, including ultra-filtration membrane systems. | 15a.png 15b.png
16 | -0.93237 | 34.8122 | Rainwater collection and treatment by Biosand/Biochar and UV LED system | Kenya | Nyamesocho rural village, Bomachoge Borabu constituency, Kisii County, Kenya | Paul Onkundi Nyangaresi and Sara E. Beck, The University of British Columbia | September 2022- present | Although water is available in the community in the rural village of Nyamesocho, Kisii County, Kenya, residents must walk long distances (>1 km) through steep terrain to fetch water. During the rainy season, water from the springs and surface streams is often colored and with high turbidity; in fact, it is highly contaminated. The collected rain water is commonly stored in polystyrene tanks, metal jerry cans, clay pots, and other water storage containers, therefore, the rainwater is often collected from such roofs. This project was designed to collect, filter and disinfect rainwater by ultraviolet light emitting diodes (UV LED), including removing odors, for use at household point of use. | The rainwater treatment consisted of biosand/biochar, and flow-through UV LED water filtration/disinfection systems. The biosand/biochar system helped in removing suspended particles collected from the roof that can hinder UV light penetration into the water. The top of the 5000 L rainwater collection tank was covered with a mosquito net to filter large debris and particles that may enter the tank. Then, the rainwater, controlled by an automatic water level control valve, passed through different layers of gravel, sand, and charcoal placed inside a 100 L polystyrene tank before being collected in another clean 100 L polystyrene tank, followed by a UV LED disinfection unit. The UV LED disinfection system contained UV LEDs emitting at 280 nm, and had a flow rate of 2 gpm. For continuous operation of the UV LED system, it was powered by automatic interchangeable electricity from both solar panels, and grid lines. Although the cost of the treatment system seemed expensive, the installation and operation were easy. | Availability and cost - In general, UV LED water disinfection systems are inaccessible and expensive not only in Kenya, but elsewhere in Africa. The system used in this work was purchased from the USA and currently costs approximately 200 USD, which is not affordable to most people in the local community, especially within a household, who earn less than 1 USD per day. However, when given options to choose between chlorine and UV treated water, they were in favor of the UV treated water since both taste and smell of the chlorinated is undesirable for them. Electrical power - Although most of the local communities in the rural village at Nyamesocho are connected to grid line electricity, the electricity is not continuous, which affects the functioning of the UV LED disinfection system. | 16a.jpg 16b.jpg 16c.jpg 16d.jpg 16e.jpg
17 | 40.1155 | -105.3875 | Bench testing and pilot demonstration in Rural Jamestown, Colorado | USA | Jamestown, CO, USA | Design of Risk-reducing, Innovative-implementable Small-system Knowledge (DeRISK) Center, led by University of Colorado Boulder Dr. Karl Linden, karl.linden@colorado.edu Dr. Natalie Hull, hull.305@osu.edu | January 2017 – February 2018 | The world’s first commercial UV-C LED water disinfection reactor was studied over a year-long demonstration test, and performance was compared side-by-side with an existing chlorination system at a small water treatment plant in Colorado serving about 300 people. The UV-C LED disinfection system was validation tested using MS2 bacteriophage inactivation over a range of flow rates and water UV transmittances. The reactor was also challenge-tested with MS2 periodically during the year-long demonstration. | The reactor (PearlAqua by Aquisense) model 25G is an NSF International 61- and IP65-certified UVC LED water disinfection system with a maximum operating pressure of 100 psi and a pressure drop at maximum flow (12 lpm) of 1.3 psi (Aquisense Technologies, 2016). It is rated for operating in water temperatures ranging from 0 to 50°C, connects with ½-in. (outer diameter female national pipe thread [FNPT]) fittings, weighs 3.3 lb, and measures roughly 6 × 6 × 6 in. for the entire system. The reactor operates in upflow where water passes through an internal diffuser before irradiation, can be mounted with a spring-loaded bracket, and is powered by a single cable from the UVinaire LED module to a standard outlet (120 V and 60 Hz). The power cable has a converter that supplies 12 V DC to the UVinaire, with 2.5 A maximum current and 26 W nominal power consumption. The UVinaire houses the internal electronics, fan, heat sink, and array of LEDs that irradiate through a quartz window to the reactor interior. The outside of the UVinaire has two visible LED indicator lights coded for various electronic warnings to indicate the status of the system and LEDs. The UVinaire has an internal 4–20 mA current loop that can be used to measure the lamp life remaining or for remote monitoring and operation. Before testing, the total output power of the UVinaire was approximately 0.25 W. | This study of a flow-through UV LED disinfection reactor indicated the resilience and disinfection effectiveness of UV LEDs, operated continuously for nearly one year with zero maintenance, with an estimated electrical cost of less than $25 to disinfect water flowing at 0.5 LPM, at an MS2 bacteriophage reduction equivalent dose (RED) by LP UV of at least 40 mJ/cm2. Disinfection performance was maintained (and was actually better than predicted) even when turbidity of the influent was greater than 1 NTU. UV LEDs could be particularly useful to help utilities with low mineral source waters to minimize fouling potential and maximize disinfection and public health protection while minimizing chlorine use and therefore disinfection byproduct formation potential. | 17a.jpg 17b.jpg

## Sheet1
| Latitude | Longitude | Location | Country | Contributor | Date of Installation | Number of Units | Brief summary | Background (geography, community, governance) | The Need (The challenge that UV is meant to address and what made UV suitable) | The UV System (description of the UV technology, including things like monitoring/maintenance strategy, flow rate, power source, performance, or others as appropriate) | Recommendations (or lessons learned. The outcome of the system and what is needed for more widespread adoption of UV) | Picture
Case study 1 Oliver Lawal Mitch Hansen - AquiSense | ND | ND | ND | Gulu, located in Northern Uganda in the Western Uganda's Kyegegwa district | Aquisense technologies (Oliver lawel) and ASEI (African STEM Education Initiative ) | ND | ND | The ASEI (NGO, African ATEM Education Initiative) tighter with Aquisense technologies are provides clean and safe water accessible to schools and hospitals across Uganda, which located between Kenya and the Democratic of the Congo. Their aim is to promote the lifelong health of children and communities in a country that nearly 70% of citizens are without access to clean water. | Located in inland Africa, between Kenya and the Democratic Republic of the Congo, Uganda has a population of over forty-seven million people. While in recent years there have been strides made by the government and other organizations in an effort towards development, potable water remains a scarce resource. Nearly 70% of citizens are without access to clean water. In Uganda, only half of the healthcare facilities treat water to make it suitable for drinking. Municipal water systems are rare and difficult to install, and bottled water is considered a luxury in the majority of communities. This is where NGOs, such as the African STEM Education Initiative (ASEI), lend a helping hand to local communities. The goal of the ASEI is to provide Ugandan students with the resources needed to advance their knowledge in STEM; therefore, directly aiding in the development of communities that house facilities such as schools and hospitals across the country. | One of the primary goals of ASEI is to provide clean drinking water to people, which will help to promote the lifelong health of children and communities in Uganda. Installing two PearlAqua AutoMate units, developed and manufactured by AquiSense Technologies, in a healthcare center in Western Uganda's Kyegegwa district and in a primary school in the community of Gulu, located in Northern Uganda, has boosted the access to clean drinking water. | ASEI used a 12V/20W DC solar system, and in some cases grid electricity. Pre-filtration is done using bio-filters and cartridge filters before it is passed through the UV-C units at a flow rate of 3.5 LPM by Aquisense technologies the selected unite was PearlAqua AutoMate. Regular surveys are done to ascertain performance and do evaluation. ASEI will now integrate UV-C units into modular micro-factories with the ability to produce >50,000 liters of treated water per month, which will be leased to water vendors to sell water at a few cents. | A few things that ASEI has learned through this process and will be implementing in the future is UV-C units and filters need to be enclosed or they are at risk of being destroyed by end users. Specially designed power cables with proper voltage controls should be used or there is a risk that the circuit boards are destroyed. Prior to any installations, it should be ensured that power and water are well managed to limit the possibility of electrical shocks. Looking forward, ASEI is planning on continuing their mission and hopes to broaden the effects of clean drinking water to more people throughout Uganda. | CS1 #1 - CS1 #13
Case study 2- Kumiko Oguma - UofTokyo | 10.404940°N, 122.579103°E. |  | https://www.google.com/maps/place/Panubulon+Island/@10.4049453,122.5769143,17z/data=!4m5!3m4!1s0x33ae9056925da879:0x39290a9527b1f73e!8m2!3d10.4052778!4d122.5788889 | Panobolon Island, Guimaras, Western Visayas, Philippines | Kumiko Oguma and Bernice Mae Yu Jeco-Espaldon | ND | ND | In Panobolon Island, Philippines, UofTokyo team leading by Kumiko Oguma and Bernice Mae Yu Jeco-Espaldon an ground water harvesting system that based of off grid UV-LED technology that powered only by the sun installed in a different places in order to provide safe drinking water to all the island citizen. the islanders were encouraged to observe the setting up of the system to provide the tools for implementation and maintenance the systems by themselves | Pilot tests of a solar-powered UV-LED water disinfection system was conducted in Panobolon Island, an off-the-grid island in the Guimaras, Western Visayas, Philippines. Groundwater was harvested from dug wells and then tested for coliform count before and after UV-LED irradiation. The long-term aim is for the island users to learn how to operate and maintain the system themselves for sustainability. | in Panobolon Island, we frequently detected E. coli in sampled wells of more than 1 CFU per 100 mL. During our pilot sampling in September 2018, all the 9 selected wells were positive with E. coli. Also, our DNA sequencing of bacterial isolates from a sampled island well suggested the presence of Shigella flexneri, a pathogen which can cause foodborne and waterborne diseases [2]. Because the island has no access to the national power grid, solar-powered UV-LED disinfection system is a suitable technology for islands. | The flow-through module used contains a single 280-nm LED, rated to operate at 12V, 350mA. It has a hydraulic retention time of 1.23 s and was designed to disinfect flowing water at 2 L/min. The UV-LED was powered by a 12V-regulated, 150-W commercial Si solar panel. | tests, the following are proposed for the final implementation of the PV-powered UV-LED water disinfection system: a) A single UV-LED flow-through module was not enough to achieve wild-type E. coli inactivation, as treated water was still E. coli positive on occasion. Another module with higher inactivation performance would be preferable. Or, increasing the number of current module and connect them in cascaded flow configuration would work; b) Photoreactivation under strong sunlight can be an issue in the field. Sunlight protection measures are to be taken. c) Seasonal change of both groundwater quality and solar radiation is to be monitored by conducting the field test in the island in a span of at least one (1) year. | CS2 #1-CS2#3
Case study 3 - Blatchley and Rachel - Purdue | ND | ND |  | Dominican Republic | Rachel E. Gehr,Ernest R. Blatchley III |  |  |  |  | Treating the rainwater to a potable quality was the easiest of the encountered challenges. The greatest barrier to project success perhaps lies within the choice of installing these systems in elementary schools. Although they are central to the communities both socially and geographically, the academic calendar leaves the systems unused during summer and winter breaks. This lack of operation often results in equipment failure, requiring maintenance or replacement. Operators that know how to resolve these issues often change due to school staff turnover, but new operators are not sufficiently trained after accepting the role. Parents of the schoolchildren have required certifications from Dominican labs proving the water’s potability, but these labs are difficult to find in-country. Finally, no sustainable business model has been developed due to the complication that water cannot be sold from school property. These problems may all be solved by having “boots on the ground,” so to speak. Ideally, there would be a Dominican-native employee to monitor all installed systems year-round, perform maintenance, conduct water quality testing, and communicate with Purdue. |  | While the engineering portion of the project was relatively easy to design and implement, it will not be successful without trust from community members and year-round use and maintenance. The systems require regular operation and water quality testing to ensure each component is working properly. This can be achieved with the support of a full-time operator who oversees the four locations and communicate with the Purdue team. Before this project can be implemented in other regions of the DR, the project must gain community investment in the importance of potable water and commitment to operating the system on a daily basis. | CS 3 #1=CS 3 #3
Case study 4 - Greg Sayles & Jim Goodrich - EPA | [12 empty] | Bottled water in Western KY Complete deployment at Western KY Location Connecting UV to WOW Cart Treatment Train in Easter KY with UV Eastern Ky Deployment Proposed Lily Pad Concept in Kentucky Western KY Deployment WOW Cart and Mobile Kitchen in Western KY WOW Cart Challenge Testing WOW Cart providing and mobile showers in Western KY WOW Cart_generator_mobile showers